Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Biamp ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Biamp, 9300 SW Gemini Dr., Beaverton, OR 97008; Phone: (800) 826-1457; Website: www.biamp.com; Email: biampinfo@biamp.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 275119 - SOUND MASKING SYSTEMS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, LEED v4.1, IgCC, and Green Globes.

GENERAL

SUMMARY

Section Includes:

Networked Sound Masking Systems using direct field (downward firing) high impedance emitter distribution.

Networked Sound Masking Systems using direct field (downward firing) individually addressable emitter distribution.

Networked Sound Masking Systems using direct field (downward firing) 70-volt loudspeaker distribution.

Networked Sound Masking Systems using indirect field (above ceiling) individually addressable loudspeaker distribution.

Networked Sound Masking Systems using indirect field (above ceiling) 70-volt loudspeaker distribution.

Networked Hybrid Masking Systems utilizing two or more systems described above within a single network.

Products Installed, but Not Furnished, under This Section:

See Section 260553 "Identification for Electrical Systems" for electrical equipment.

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Retain subparagraph below if retaining "Preinstallation Conference" Paragraph in "Preinstallation Meetings" Article. If Project is using Owner-provided Division 01, revise to indicate location where Owner's conference procedures are specified, or delete subparagraph and specify the conference procedures under "Preinstallation Conference" Paragraph.

[Section 013100 "Project Management and Coordination"] <Insert Section number and title> for preinstallation conference procedures.

DEFINITIONS

Do not duplicate common acronyms, abbreviations, and terms defined in Section 270010 "Supplemental Requirements for Communications."

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

Amplifier: An electronic device required to amplify audio levels from certain masking controllers to drive masking emitters or loudspeakers to a usable sound pressure level.

Authorized Dealer: The company chosen to provide all sound masking system products described in Part 2. This dealer must be authorized by the manufacturer to provide, install, maintain, and warrant the products specified herein.

Direct Field Masking System: A sound masking system composed of emitters or loudspeakers that emit masking noise directly into a masking environment without permeating through an obstruction such as a ceiling or floor tile.

Hybrid Masking System: A sound masking system composed of direct field and indirect field masking systems monitored and controlled by a common network interface.

Indirect Field Masking System: A sound masking system composed of loudspeakers that emit masking noise into a space either above or below the masking environment and permeate into the masking environment through an obstruction such as a ceiling.

Loudspeaker or Emitter: These terms are used interchangeably to indicate a device in the sound masking system that emits masking sound and voice paging or music.

Sound Masking System: The electronic equipment and emitters or loudspeakers used to generate, distribute, and control masking sound throughout a treated area.

Manufacturer: The company that manufacturers the sound masking system products.

Masking Controller: A networkable electronic device that provides audio feeds to masking emitters or loudspeakers. Audio may include masking noise, background music, or paging or a combination thereof.

Max Level Variation: The maximum variation, in decibels, of the equalized overall level or one-third octave level allowed in the masking system.

Network: An Ethernet based IP transport to facilitate communications from a PC to the sound masking system or between controllers within a sound masking system. The network must support system configuration, system control, and audio transport between devices.

Network Switch: A network device when connected to masking controllers allows controllers to share control and audio communications and, when connected to a computer, facilitates setup and control of an entire system from a single connection point.

Paging Microphone/Paging Station: When connected to a masking controller or through a network switch, sends paging messages to one or more masking zones.

Sound Masking System Designer: The person or team responsible for design of the sound masking system.

Spatial Uniformity: A condition where the sound pressure levels throughout a defined space do not vary significantly from a specified sound pressure level.

Spectral Uniformity: A condition where the sound pressure in each one-third octave band does not vary significantly from the specified one-third octave sound pressure level.

SPL: Sound pressure level in dB re 0.00002 Pa (0.0002 microbar).

Target Level Variation: The variation, in decibels, of the equalized overall level or one-third octave level used as a target in the sound masking system.

Temporal Uniformity: At a given position, a condition where the average sound pressure level measured over a short time interval does not differ significantly from the average sound pressure level measured over a long time interval.

Zone: One or more emitters or loudspeakers assigned to a masking controller and operating as a group.

REFERENCES

ANSI S1.4 - Specification for Sound Level Meters. Calibrated Type 1 or Type 2.

ANSI S1.6 - Preferred Frequencies, Frequency Levels, and Band Numbers for Acoustical Measurements.

ANSI S1.11 - Specification for Octave-Band and Fractional-Octave-Band Analog and Digital Filters.

ASTM E1130-16 - Standard Test Method for Objective Measurement of Speech Privacy in Open Plan Spaces Using Articulation Index (Updated).

ASTM E1374-18e1 - Standard Guide for Office Acoustics and Applicable ASTM Standards (Updated).

ASTM E1573-22 - Standard Test Method for Measuring and Reporting of Masking Sound Levels Using A-Weighted and One-Third-Octave-Band Sound Pressure Levels (Updated).

ASTM E2638-10(2017) - Standard Test Method for Objective Measurement of the Speech Privacy Provided by a Closed Room.

CE Code - Canadian Electrical Code as Published by the Canadian Standards Association referencing 24th Edition / 2018.

CSA - Canadian Standards Association

ISO - International Organization for Standardization

NEC - National Electrical Code

UL 2043 - Standard for Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces.

QUALIFICATIONS

An authorized dealer for the major product components and is certified by the manufacturer to perform installation, setup, maintenance, and warranty.

A verifiable history of successful installations of at least three projects of similar scope and size.

Provide the necessary personnel experienced in operating the required test measurement equipment outlined herein to configure, test, and calibrate the sound masking system.

During the warranty period, maintain two or more technicians who are certified for the product(s) under warranty as stated in "Warranty for Sound Masking Systems" Article.

PREINSTALLATION MEETINGS

Preinstallation conference or preinstallation coordination meetings should be held for offices occupied by government or government's contractors, when certification of spaces for handling controlled information is required after construction, to ensure that Installer complies with required processes and procedures to obtain certification from the start.

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

Retain "Preinstallation Coordination Meeting(s)" Paragraph below if Work of this Section does not justify a full preinstallation conference as specified in Section 013100 "Project Management and Coordination," but would benefit from a smaller coordination meeting. Consider videoconference option if Project requires social distancing for meetings for infection control.

Preinstallation coordination meetings may be required for offices occupied by government or offices occupied by government contractors that require certification of spaces after construction.

Preinstallation Coordination Meeting(s): For sound masking systems. Conduct meeting(s) [as videoconference] [or] [at Project site] <Insert location> before <Insert construction activity>.

Attendees: Installers, fabricators, representatives of manufacturers, and administrants for field tests and inspections. Notify Architect[, Construction Manager] [, and Owner's Commissioning Authority] of scheduled meeting dates.

ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

Product Data: For each system in paragraph 1.1.A.

Manufacturer's detailed technical data sheets for all major sound masking system components, including material descriptions, applicable product pictures or drawings, finishes, electrical characteristics, and regulatory certifications.

Shop Drawings: For each system in paragraph 1.1.A.

Complete floor plan and/or reflected ceiling plan drawing(s) denoting, at minimum, device locations that have been prepared by the sound masking system designer based on the sound masking system manufacturer guidelines.

Mounting details for all devices.

Wiring diagrams connecting all devices.

Retain first paragraph below if required.

Field quality-control reports.

Retain paragraph below if required to attain sustainability rating or to track sustainability submittals.

Sustainable design submittals.

INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Manufacturers' Published Instructions:

Sound masking equipment.

Field Reports:

Manufacturer's field reports for field quality-control support.

Manufacturer's field reports for system startup support.

Field reports for software and firmware upgrades.

CLOSEOUT SUBMITTALS

Submittals for record documents, operation and maintenance data, software, and software documentation are specified in Section 270010 "Supplemental Requirements for Communications."

All final control processor settings, emitter or loudspeaker zone maps, loudspeaker tap settings, one line diagrams, operational instruction, and testing results.

Location of each sound pressure level measurement, privacy index measurement, and spatial uniformity measurement referenced within the final documents on the zone map.

Media with each documentation set utilizing the same software version as currently installed and operating and all configuration files created by the configuration software on the same media.

Retain paragraph below if required to attain sustainability rating or to track sustainability submittals.

Sustainable design closeout documentation.

REGULATORY AGENCY APPROVALS

Retain this article when review and approval of Contractor's submittals by authorities having jurisdiction is required.

Retain one of two paragraphs below. Retain first paragraph if Contractor's submittals are prepared by Contractor's professional engineer who is recognized by authorities having jurisdiction as designer of record for sound masking system. Retain second paragraph if Contractor's submittals require review and approval with signature and seal by Architect's professional engineer who is recognized as designer of record.

In first paragraph, obtaining approval from authorities having jurisdiction first may lead to unnecessary delays for resubmission of Contractor's submittals to authorities having jurisdiction after action by Architect. Obtaining approval from Architect first may lead to unnecessary delays for rework if Contractor's submittals are rejected by authorities having jurisdiction after action by Architect. Architects typically prefer receiving approval by authorities having jurisdiction before taking action, but likelihood and consequences of risks under Project's delivery method (e.g., design-bid-build or design-build) should be considered before retaining an option.

Submittals for sound masking systems connected to [fire alarm] [and] [mass notification] require approval by authorities having jurisdiction and must be signed and sealed by qualified life safety professional engineer responsible for their preparation. [Obtain approval by authorities having jurisdiction prior to submitting for action by Architect.] [Submit for action by Architect prior to submitting for approval by authorities having jurisdiction.]

Submittals for sound masking systems connected to [fire alarm] [and] [mass notification] require action by Architect prior to submitting for approval by authorities having jurisdiction.

WARRANTY FOR SOUND MASKING SYSTEMS

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner, after one-year correction period specified in the Contract, under Contractor's general warranty and prevailing local laws.

Verify durations of extended-warranty periods needed.

Base-Warranty Period: Installer warrants that fabricated and installed sound masking systems perform in accordance with specified requirements and agrees to repair or replace components or products that fail to perform as specified within the base-warranty period.

The installation of all equipment, cabling, and labor for an initial period of one year from the date of final acceptance unless a longer term is specified elsewhere.

Equipment to be free of faulty workmanship and defects for a minimum period of five years from date of final acceptance.

Services, including telephone support, at no charge during the duration of the initial one-year warranty period.

Semiannual visits to the site for routine adjustment and maintenance of all specified and installed systems during the initial warranty period.

Special Installer Extended Warranty: Installer warrants that fabricated and installed sound masking systems perform in accordance with specified requirements and agrees to repair or replace components or products that fail to perform as specified within extended-warranty period.

Extended-Warranty Period: From the end of the Base Warranty Period, [two] [three] [four] <Insert number> additional years; full coverage for labor, materials, and equipment.

Retain "Special Manufacturer Extended Warranty" Paragraph below if Project requires that a special manufacturer extended warranty take over when the special Installer extended warranty expires. To benefit Owner, manufacturer extended-warranty period must be longer than Installer extended-warranty period.

Special Manufacturer Extended Warranty: Manufacturer warrants that sound masking systems perform in accordance with specified requirements and agrees to provide repair or replacement of components or products that fail to perform as specified within extended-warranty period.

PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

NETWORKED SOUND MASKING SYSTEMS - APPLIES TO ALL SYSTEMS

Description: Electronic noise generators and associated controls for simultaneously operating multiple masking noise emission devices throughout facility.

Basis-of-Design Product: The design for this specification is based on the Biamp line of sound masking products. Comparable products from manufacturers below may be considered provided they meet all the criteria listed within this specification.

AtlasIED

Lencore.

Logison.

<Insert manufacturer's name>.

Performance Criteria:

Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction and marked for intended location and application.

General Characteristics:

Include all masking, signal generation, signal processing, amplification, and emitters or loudspeakers with associated wiring, software, and controls.

The equipment to be procured from a single manufacturer.

The system to be composed of one or more logical zones capable of configuration and naming by the sound masking contractor. More than one physical output, including those from multiple control processors to be configured and assigned as a single zone. Each output within the zone to be controlled independently as to masking spectrum and level.

The system to be capable of automatically scheduling system parameter adjustments, including initial acclimatization, on a per-zone basis.

Control for the system to be facilitated through any combination of front panel hardware interface, manufacturer configuration software, and/or a web browser-based software interface.

The system to generate, amplify, and distribute a minimum of four noncorrelated sound masking signals on adjacent emitters or loudspeakers when their spacing is 12 ft (3.65 m) or less. In this situation, adjacent emitter or loudspeaker devices to not reproduce coherent sound masking signals.

The system to be capable of accepting, at minimum, two external analog microphone or line level audio sources from ancillary audio equipment with control on a per-zone basis.

The system zones to be determined by the functional requirements of each area(s) with separate independent level control for each zone as indicated by the Project documents.

A new zone with separate level control to be required in instances where a change in emitter or loudspeaker mounting or ceiling height causes a greater than 0.5 dB increase or drop in level or where emitter or loudspeaker density changes from one area to another. This usually translates to a varying device level height of about 6 inches (152 mm) in a typical ceiling environment.

CONTROL PROCESSOR

Sound Controller:

General Characteristics:

The sound controller to be DSP based.

The sound controller to provide multi-zone processing that will facilitate adjustment of the masking level on a per-zone basis in 0.5 dB increments.

The controller to provide per-zone scheduling function via internal clock source and/or NTP server, which can adjust the masking signal levels. Scheduling will, at a minimum, adjust for separate weekday and weekend level settings.

The sound controller to provide an automatic, incremental level adjustment feature, allowing a gradual, one-time change of masking levels to commence upon completion of system commissioning, acclimating occupants to a newly sound masked environment (initial acclimatization).

The sound controller to be separately capable of one-third octave equalization adjustment of the sound masking spectrum for each output as defined in Chart One of this specification.

The sound controller to have two configurable network ports.

A single port configuration to simultaneously support communications, control, and audio, either AVB or Dante© (if applicable) with the second port being unused.

A dual port configuration to support audio on one network port and communications and control on the second network port.

Separate MAC addresses to be available for control, AVB and Dante© in either port configuration.

The sound controller to have at least two mic/line level analog audio source inputs usable for paging or background music with phantom power available for microphones. The audio source inputs to be routable to other controllers over the audio network. A separate one-octave band equalizer, independent from the sound masking equalizer, to be provided for adjustment of each audio source separate from the masking equalization.

The sound controller to accept six external audio channels via an eight-channel audio network transport usable for background music or paging. The audio transport to be based on industry standard 802.1X protocols. Dante© may be used as an acceptable alternate protocol for controllers that support Dante©. Routing of one or more audio channels to specific masking zones to be configured via the controller software.

The sound controller to have the capability to mute or otherwise disable the sound masking signal and any other audio signals using a dry contact closure from a third-party source such as a fire alarm control panel (FACP). In a multiple processor system, a single contact closure at one processor will mute audio at all other processors when network communication exists.

Means of control for the masking controller will be facilitated through any combination of front panel hardware interface, manufacturer configuration software, and/or a web browser-based software interface.

Third-party supervision and control of the masking system will be facilitated via the industry standard RESTful API syntax. This feature will be protected from unauthorized access via multi-role security credentials.

The sound controller to be networkable over standard Ethernet with dual network ports and will support a minimum of 90 controllers on a single network.

The sound controller to be capable of TCP/IP network connectivity via DHCP or Static IP address.

The sound controller to support 802.1X port authentication for network security.

The sound controller to support certificates. Users may select a Root or Client certificate based on the security requirements of the organization.

The sound controller to support multi-role user authentication passwords.

The sound controller to support fault reporting of trouble conditions.

The sound controller to feature a nonvolatile memory, capable of storing all system settings in the case of power disconnect.

The controller to be CE marked, UL listed, and RoHS compliant.

The controller to be TAA compliant and GSA eligible.

The controller to be covered by a manufacturer five-year warranty.

System Specific Characteristics:

Retain first subparagraph below if the Networked Sound Masking Systems using direct field (downward firing) high impedance emitter distribution solution are chosen.

Networked sound masking systems using direct field (downward firing) high impedance emitter distribution.

The sound controller to provide a minimum of four noncorrelated masking signal outputs per-zone.

For passive direct field emitter solutions, the masking controller to support a maximum of 60 emitters on each of two runs for each masking zone with a maximum cumulative cable distance of 1000 ft (305 m). Where this distance is exceeded, some emitters to be broken off into a separate run on that zone.

For active direct field emitter solutions, the masking controller to support a maximum of 50 emitters on each of two runs. Each run to be further divided by a power insertion device that injects DC power in each emitter line and has two outputs to power up to one half the number of emitters allowed in a run 25. The maximum cumulative cable distance from the power inserter to the last emitter in each of the two legs of the run to be 400 ft (122 m). Where this distance is exceeded, some emitters to be broken off into a separate run on that zone.

The sound controller to provide a factory default sound masking spectrum as defined in Chart One of this specification.

The sound controller to include factory-set equalization for each loudspeaker output, with no in-field loudspeaker equalization normally necessary.

The sound controller to include a UL/CUL/CE listed, 120-240VAC 50/60 Hz power supply.

A wall mount bracket to be included with the masking controller.

Retain first subparagraph below if the Networked Sound Masking Systems using direct field (downward firing) individually addressable emitter distribution are chosen.

Networked sound masking systems using direct field (downward firing) individually addressable emitter distribution.

The sound controller to provide a minimum of eight noncorrelated masking signal outputs per controller. Each output to be rated at 4Ω and to be designed to power one direct field masking loudspeaker.

The masking controller to be rated for UL 2043 and be designed for installation within a plenum ceiling space.

The masking controller to be powered via standard PoE+ power injector or network switch.

The masking controller to support a maximum of eight loudspeakers per controller.

The sound controller to provide a factory default sound masking spectrum as defined in Chart One of this specification.

The sound controller to include factory-set equalization for each loudspeaker zone, with no in-field loudspeaker equalization normally necessary.

A ceiling grid mounting bracket to be included with the masking controller.

Retain first subparagraph below if the Networked Sound Masking Systems using direct field (downward firing) 70-volt loudspeaker distribution are chosen.

Networked sound masking systems using direct field (downward firing) 70-volt loudspeaker distribution.

The sound controller to provide a minimum of eight noncorrelated masking signal outputs per controller.

The masking controller to support a maximum of eight masking zones per controller.

Each masking zone output to be analog line level designed to drive a 70-volt amplifier. The number of loudspeakers supported by a single controller to be determined by the capabilities of the 70-volt amplifier(s) that are chosen.

The sound controller to include a UL/CUL/CE listed, 120-240VAC 50/60 Hz power supply.

A rack-mount bracket to be included with the masking controller.

Retain first subparagraph below if the Networked Sound Masking Systems using indirect field (above ceiling) individually addressable loudspeaker distribution are chosen.

Networked sound masking systems using indirect field (above ceiling) individually addressable loudspeaker distribution.

The sound controller to provide a minimum of eight noncorrelated masking signal outputs per controller. Each output to be rated at 4Ω and be designed to power up to eight indirect field masking loudspeakers.

The masking controller to be rated for UL 2043 and be designed for installation within a plenum ceiling space.

The masking controller to be powered via standard PoE+ power injector or network switch.

The masking controller to support a maximum of 16 loudspeakers per controller.

A ceiling grid mounting bracket to be included with the masking controller.

Retain subparagraph below if the Networked Sound Masking Systems using indirect field (above ceiling) 70-volt loudspeaker distribution are chosen.

Networked sound masking systems using indirect field (above ceiling) 70-volt loudspeaker distribution.

The sound controller to provide a minimum of eight noncorrelated masking signal outputs per controller.

The masking controller to support a maximum of eight masking zones per controller.

Each masking zone output to be analog line level designed to drive a 70-volt amplifier. The number of loudspeakers supported by a single controller to be determined by the capabilities of the 70-volt amplifier(s) that are chosen.

The sound controller to include a UL/CUL/CE listed, 120-240VAC 50/60 Hz power supply.

A rack-mount bracket to be included with the masking controller.

EMITTER AND LOUDSPEAKER TYPES

Retain first paragraph below if the Networked Sound Masking Systems using direct field (downward firing) high impedance emitter distribution solution are chosen utilizing passive emitters.

1.25 inches (32 mm) passive emitter, direct field, daisy chainable, in-ceiling or surface mount supporting masking only.

The emitter to be designed for direct field operation, radiating directly into the occupied space.

The emitter driver to be a nominal 1.25 inches (32 mm) diameter with an overall housing diameter of 3.25 inches (83 mm).

The emitter to be purpose built to interface with its associated controller and cannot be used with any other controlling device.

The nominal frequency response of the emitter to be 200 Hz to 5 kHz.

The nominal dispersion of the emitter to be at least 170 deg F (77 deg C) below 4.2 kHz.

The emitter housing to be capable of mounting directly into acoustic ceiling tile materials, surface mounted, pendant mounted, structural beam mounted, or hard surface ceiling mounted utilizing optional manufacturer supplied accessories. Provide seismic rated mounting where required by jurisdiction.

The emitters to be spaced evenly between 8 and 12 ft (2.45 and 3.65 m) apart as recommended by the product manufacturer based on site conditions and ceiling heights and below finished ceiling obstructions to meet the performance requirements. Refer to "Installation" Article for direct field masking emitters or loudspeakers installation requirements.

The emitter to be capable of producing minimum sound pressure levels and frequency spectrum for emitters and as measured at an above finished floor height of 4 ft (1.2 m) regardless of ceiling type, ceiling height, or presence of obstructions. Refer to paragraph 3.6.C of this specification for more information on the installation requirements.

The emitter to include DIP switches to provide 3 dB decrements of level for up to 9 dB of level reduction for easy micro-zoning.

The emitter to include internal circuiting to support the routing of four noncorrelated masking channels so that adjacent emitters do not emit the same noise source, minimizing phase effects between emitters.

The emitter and all mounting accessories to be UL 2043 compliant.

The emitter to require a single, multi-conductor, low-voltage cable meeting NEC Class 2 requirements for low-voltage distribution. The cabling to be rated for use in plenum spaces.

The emitter to be available in white (standard) or black finish. An optional emitter cap to be available that can be painted to match a particular ceiling color if required.

The emitter to include a manufacturer-supported five-year warranty.

Retain first paragraph below if the Networked Sound Masking Systems using direct field (downward firing) high impedance emitter distribution solution are chosen utilizing active emitters.

1.25 inches (32 mm) active emitter, direct field, daisy chainable, in-ceiling or surface mount supporting masking, paging, and background music.

The emitter to be designed for direct field operation, radiating directly into the occupied space.

The emitter driver to be a nominal 1.25 inches (32 mm) diameter with an overall housing diameter of 3.25 inches (83 mm).

The emitter to be purpose built to interface with its associated controller and cannot be used with any other controlling device.

The nominal frequency response of the emitter to be 105 Hz to 12 kHz.

The nominal dispersion of the emitter to be at least 170 deg F (77 deg C) below 4.2 kHz.

The emitter housing to be capable of mounting directly into acoustic ceiling tile materials, surface mounted, pendant mounted, structural beam mounted, or hard surface ceiling mounted utilizing optional manufacturer supplied accessories. Provide seismic rated mounting where required by jurisdiction.

The emitters to be spaced evenly between 8 and 12 ft (2.45 and 3.65 m) apart as recommended by the product manufacturer based on site conditions and ceiling heights and below finished ceiling obstructions to meet the performance requirements. Refer to "Installation" Article for emitter installations.

The emitter to be capable of producing minimum sound pressure levels and frequency spectrum. Refer to paragraph 3.6.C of this specification for 1.25 inches (32 m) emitters measured at an above finished floor height of 4 ft (1.2 m) regardless of ceiling type, ceiling height, or presence of obstructions.

The emitter to include DIP switches to provide 1.5 dB decrements of level for up to 4.5 dB of level reduction for easy micro-zoning.

The emitter to include internal circuiting to support the routing of four noncorrelated masking channels so that adjacent emitters do not emit the same noise source, minimizing phase effects between emitters.

The emitter and all mounting accessories to be UL 2043 compliant.

The emitter to require a single, multi-conductor, low-voltage cable meeting NEC Class 2 requirements for low-voltage distribution. The cabling to be rated for use in plenum spaces.

The emitter to be available in white or black finish. The emitter is not paintable.

The emitter to include a manufacturer-supported five-year warranty.

Retain first paragraph below if the Networked Sound Masking Systems using direct field (downward firing) individually addressable emitter distribution are chosen.

1.25 inches (32 mm) emitter, direct field, individually controlled, in-ceiling or surface mount supporting masking, paging, and background music.

The emitter to be designed for direct field operation, radiating directly into the occupied space.

The emitter driver to be a nominal 1.25 inches (32 mm) diameter with an overall housing diameter of 3.25 inches (83 mm).

The emitter to be purpose built to interface with its associated controller and cannot be used with any other controlling device.

The nominal frequency response of the emitter to be 125 Hz to 12 kHz.

The nominal dispersion of the emitter to be at least 170 deg F (77 deg C) below 4.2 kHz.

The emitter housing to be capable of mounting directly into acoustic ceiling tile materials, surface mounted, pendant mounted, structural beam mounted, or hard surface ceiling mounted utilizing optional manufacturer-supplied accessories. Provide seismic rated mounting where required by jurisdiction.

The emitters to be spaced evenly between 8 and 12 ft (2.45 and 3.65 m) apart as recommended by the product manufacturer based on site conditions and ceiling heights and below finished ceiling obstructions to meet the performance requirements. Refer to "Installation" Article for emitter installations.

The emitter to be capable of producing minimum sound pressure levels and frequency spectrum. Refer to paragraph 3.6.C of this specification for 1.25 inches (32 m) emitters measured at an above finished floor height of 4 ft (1.2 m) regardless of ceiling type, ceiling height, or presence of obstructions.

The emitter and all mounting accessories to be UL 2043 compliant.

The emitter to require a single, two-conductor 18 gauge unshielded, low-voltage cable meeting NEC Class 2 requirements for low-voltage distribution. The cabling to be rated for use in plenum spaces.

The emitter to be available in white or black finish. The emitter is not paintable.

The emitter to include a manufacturer-supported five-year warranty.

Retain first paragraph below if the Networked Sound Masking Systems using direct field (downward firing) 70-volt loudspeaker distribution are chosen.

3 inches (76 mm) driver, 70-volt, direct field surface mount loudspeaker supporting masking, paging, and background music.

The loudspeaker to be direct field, radiating directly into the occupied space.

The loudspeaker driver to be full range with a nominal 3 inches (76 mm) diameter.

The loudspeaker to be optimized to interface with the associated controller and to not be used with any other controlling device.

The loudspeaker to be capable of surface mounting via the included U-bracket. Pendant mounting can be attained by utilizing threaded rod attached to the U-bracket. Provide an additional safety-rated cable where required by code.

The loudspeakers to be spaced evenly between 6 and 10 ft (1.8 and 3.1 m) apart as recommended by the product manufacturer based on site conditions and ceiling heights and below finished ceiling obstructions to meet the performance requirements. Refer to "Installation" Article for direct field loudspeaker installations.

The loudspeaker to be capable of producing minimum sound pressure levels and frequency spectrum. Refer to paragraph 3.6.C of this specification for drivers measured at an above finished floor height of 4 ft (1.2 m) regardless of ceiling type, ceiling height, or presence of obstructions.

The loudspeaker to require a single, two-conductor 18 gauge or greater unshielded, low-voltage cable meeting NEC Class 2 requirements for low-voltage distribution. The cabling to be rated for use in plenum spaces.

The loudspeaker to be available in white or black finish. The loudspeakers are not paintable.

The loudspeaker to include a manufacturer-supported five-year warranty.

Retain first paragraph below if the Networked Sound Masking Systems using indirect field (above ceiling) individually addressable loudspeaker distribution for plenum spaces over 18 inches deep are chosen.

5.25 inches (134 mm) driver, 8Ω, indirect field (above ceiling) loudspeaker for masking.

The loudspeaker to be mounted above a finished acoustic ceiling tile ceiling, radiating into the plenum space. The plenum space to be at least 18 inches (134 mm) deep from finished ceiling to deck.

The loudspeaker driver to be full range with a nominal 5.25 inches (134 mm) in diameter.

The loudspeaker enclosure to be ported and formed from a seamless 1 mm cold rolled steel plate material with a powder coated finish. The enclosure to measure 8.5 inches (216 mm) in diameter by 5 inches (127 mm) high. The enclosure to be internally acoustically dampened.

The loudspeaker impedance to be a nominal 8Ω.

The loudspeaker frequency response to be a nominal 125 Hz to 10 kHz.

The loudspeaker sensitivity to be a nominal 91.9 dB 1W/1M.

The loudspeaker to be optimized to interface with the associated controller and to not be used with any other controlling device.

The loudspeaker to include a four-point suspension system with hanging chain for ease of installation and leveling.

The loudspeakers to be spaced as recommended by the product manufacturer based on plenum depth and type of acoustic ceiling tile. Final spacing to meet the performance requirements. Refer to "Installation" Article for indirect field loudspeaker installations.

The loudspeaker to be capable of producing minimum sound pressure levels and frequency spectrum. Refer to paragraph 3.6.C of this specification for indirect field loudspeaker installations and as measured at an above finished floor height of 4 ft (1.2 m) regardless of ceiling type, ceiling height, or presence of obstructions.

The loudspeaker and all mounting accessories to be UL 2043 listed as appropriate for use in the plenum spaces where it will be mounted.

The loudspeaker to require a single, two-conductor 18 gauge unshielded, low-voltage cable meeting NEC Class 2 requirements for low-voltage distribution. The cabling to be rated for use in plenum spaces.

The loudspeaker to be available in white or black finish.

The loudspeaker to include a manufacturer-supported five-year warranty.

Retain first paragraph below if the Networked Sound Masking Systems using indirect field (above ceiling) 70-volt loudspeaker distribution for plenum spaces over 18 inches deep are chosen.

5.25 inches (134 mm) driver, 70-volt, indirect field (above ceiling) loudspeaker for masking.

The loudspeaker to be mounted above a finished acoustic ceiling tile ceiling, radiating into the plenum space. The plenum space to be at least 18 inches (460 mm) deep from finished ceiling to deck.

The loudspeaker driver to be full range with a nominal 5.25 inches (134 mm) in diameter.

The loudspeaker enclosure to be ported and formed from a seamless 1 mm cold rolled steel plate material with a powder coated finish. The enclosure to measure 8.25 inches (216 mm) in diameter by 5 inches (127 mm) high. The enclosure to be internally acoustically dampened.

The loudspeaker to include an internal transformer with 1/8W, 1/4W, 1/2W, 1W, 2W, and 4W taps at 70 volts and an external wattage selector to choose the preferred wattage.

The loudspeaker frequency response to be a nominal 125 Hz to 10 kHz.

The loudspeaker sensitivity to be a nominal 91.9 dB 1W/1M.

The loudspeaker to be optimized to interface with the associated controller and to not be used with any other controlling device.

The loudspeaker to include a four-point suspension system with hanging chain for ease of installation and leveling.

The loudspeakers to be spaced as recommended by the product manufacturer based on plenum depth and type of acoustic ceiling tile. Final spacing to meet the performance requirements. Refer to "Installation" Article for indirect field loudspeaker installations.

The loudspeaker to be capable of producing minimum sound pressure levels and frequency spectrum. Refer to paragraph 3.6.C of this specification for indirect field loudspeaker installations and as measured at an above finished floor height of 4 ft (1.2 m) regardless of ceiling type, ceiling height, or presence of obstructions.

The loudspeaker and all mounting accessories to be UL 2043 listed as appropriate for use in the plenum spaces where it will be mounted.

The loudspeaker to require a single, two-conductor 18 gauge or greater unshielded, low-voltage cable meeting NEC Class 2 requirements for low-voltage distribution. The cabling to be rated for use in plenum spaces.

The loudspeaker to be available in white or black finish.

The loudspeaker to include a manufacturer-supported five-year warranty.

Retain first paragraph below if the Networked Sound Masking Systems using indirect field (above ceiling) individually addressable loudspeaker distribution for plenum spaces under 18 inches deep are chosen.

Dual 4 inches (102 mm) by 1.5 inches (38 mm), 8Ω, indirect field (above ceiling) loudspeaker for masking.

The loudspeaker to be mounted above a finished acoustic ceiling tile ceiling, radiating into the plenum space. The loudspeaker is designed for use in ceilings where plenum space is less than 18 inches (134 mm) or where the plenum space is severely restricted due to HVAC or other obstructions.

The dual opposed loudspeaker drivers each to be full range with a nominal 4 inches (102 mm) by 1.5 inches (38 mm) dimension.

The loudspeaker enclosure to be formed from a 1 mm cold rolled steel plate material with a powder coated finish. The enclosure dimensions to be a nominal 5.25 inches (135 mm) by 6.25 inches (160 mm) by 1.8 inches (45 mm) high. The enclosure to include tuned ports.

The loudspeaker impedance to be a nominal 4Ω.

The loudspeaker frequency response to be a nominal 160 Hz to 6.3 kHz.

The loudspeaker sensitivity to be a nominal 80.7 dB 1W/1M.

The loudspeaker is optimized to interface with the associated controller and to not be used with any other controlling device.

The loudspeaker to accommodate an optional ceiling tile bridge for ceiling mounting.

The loudspeakers to be spaced as recommended by the product manufacturer based on plenum depth and type of acoustic ceiling tile. Final spacing to meet the performance requirements. Refer to "Installation" Article for indirect field loudspeaker installations.

The loudspeaker to be capable of producing minimum sound pressure levels and frequency spectrum. Refer to paragraph 3.6.C of this specification for indirect field loudspeaker installations and as measured at an above finished floor height of 4 ft (1.2 m) regardless of ceiling type, ceiling height, or presence of obstructions.

The loudspeaker and all mounting accessories to be rated to UL 2043 and CSA C22.2 No. 205-12 as appropriate for use in the spaces where it will be mounted.

The loudspeaker to require a single, two-conductor 18 gauge unshielded, low-voltage cable meeting NEC Class 2 requirements for low-voltage distribution. The cabling to be rated for use in plenum spaces.

The loudspeaker to be available in white finish.

The loudspeaker to include a manufacturer-supported five-year warranty.

Retain paragraph below if the Networked Sound Masking Systems using indirect field (above ceiling) 70-volt loudspeaker distribution for plenum spaces under 18 inches deep are chosen.

Dual 4 inches (102 mm) by 1.5 inches (38 m) driver, 70-volt, indirect field (above ceiling) loudspeaker for masking.

The loudspeaker to be mounted above a finished acoustic ceiling tile ceiling, radiating into the plenum space. The loudspeaker is designed for use in ceilings where plenum space is less than 18 inches (134 mm) or where the plenum space is severely restricted due to HVAC or other obstructions.

The dual opposed loudspeaker drivers each to be full range with a nominal 4 inches (102 mm) by 1.5 inches (38 mm) dimension.

The loudspeaker enclosure to be formed from a 1 mm cold rolled steel plate material with a powder coated finish. The enclosure dimensions to be a nominal 5.25 inches (135 mm) by 6.25 inches (160 mm) by 1.8 inches (45 mm) high. The enclosure to include tuned ports.

The loudspeaker to include an internal transformer with 1/8W, 1/4W, 1/2W, 1W, 2W, and 4W taps at 70-volts and an external wattage selector to choose the preferred wattage.

The loudspeaker frequency response to be a nominal 160 Hz to 6.3 kHz.

The loudspeaker sensitivity to be a nominal 80.7 dB 1W/1M.

The loudspeaker is optimized to interface with the associated controller and to not be used with any other controlling device.

The loudspeaker to accommodate an optional ceiling tile bridge for ceiling mounting.

The loudspeakers to be spaced as recommended by the product manufacturer based on plenum depth and type of acoustic ceiling tile. Final spacing to meet the performance requirements. Refer to "Installation" Article for indirect field loudspeaker installations.

The loudspeaker to be capable of producing minimum sound pressure levels and frequency spectrum. Refer to paragraph 3.6.C of this specification for indirect field loudspeaker installations and as measured at an above finished floor height of 4 ft (1.2 m) regardless of ceiling type, ceiling height, or presence of obstructions.

The loudspeaker and all mounting accessories to be rated to UL 2043 and CSA C22.2 No. 205-12 as appropriate for use in the spaces where it will be mounted.

The loudspeaker to require a single, two-conductor 18 gauge or greater unshielded, low-voltage cable meeting NEC Class 2 requirements for low-voltage distribution. The cabling to be rated for use in plenum spaces.

The loudspeaker to be available in white finish.

The loudspeaker to include a manufacturer supported five-year warranty.

NETWORK SWITCH

The network switch to utilize a managed architecture.

The network switch to support Layer 2 and Layer 3 switching.

The network switch to include an active AVB license.

The network switch to handle control, AVB and Dante© protocols within the same switch.

The network switch to have a minimum of eight 10/100/1000 PoE+ enabled ports, two non-PoE 10/100/1000 ports, and (2) SFP+ 1G/10G ports. All ports to be auto sensing.

The network switch to have a PoE power budget to support a minimum of eight PoE+ devices simultaneously on a single switch.

The network switch to have a switching fabric of 60Gbps or greater.

The network switch to support Link Aggregation Groups to allow multiple switches to act as a single link.

The network switch to have a dedicated web-based GUI interface to support sound masking installations.

The network switch to have a selectable fan mode to minimize fan noise based on ambient temperature and power requirements.

The network switch to be rack mountable.

The network switch to be TAA compliant.

The network switch to have a manufacturer lifetime warranty.

AMPLIFIER

Retain this article if a 70-volt loudspeaker distribution is chosen.

The amplifier to be rated to support 70-volt speakers.

Individual amplifier channels to be required for each zone where masking equalization needs adjustment due to ceiling material variations or structural variations above or below the ceiling.

Unless specifically stated in the amplifier manufacturer specifications for masking systems, each amplifier channel to be loaded to no more than 42 percent of their rated RMS power.

Level controls to be located on the back of the amplifier. No level controls to be allowed on the front of the amplifier.

Input impedance to be 8kΩ or greater.

Input sensitivity to be +4 dBu (1.23 Vrms).

Maximum input level per channel to be +24 dBu.

THD+N (1 kHz, 1dB below clip) to be less than 0.008 percent.

Channel separation at 1 kHz to be greater than 75 dB.

Input gain for 70-volt operation to be 35.2 dB.

Power output per channel to be at least 75 watts, all channels driven.

The amplifier to include a built-in limiter for each output.

The amplifier to include a switchable high pass filter rated at 70 Hz, 12 dB/octave for each channel.

The amplifier to include front panel LEDs to indicate:

Temperature status.

Limiter status.

Signal status.

Power status.

Provide the necessary quantity of amplifiers/amplifier-channels to correspond with the Project zoning/sound-masking-generator requirements.

The amplifier to be listed to conform to UL 62368-1 and CSA C22.2 No. 62368-1.

The amplifier to include a manufacturer-supported five-year warranty.

SOFTWARE AND CONTROL

The sound masking system to be capable of software control via a TCP/IP local area network connection to the Owner's local area network (LAN Infrastructure). Communication to be via industry standard Ethernet protocols. No communication via serial or proprietary bus architectures to be acceptable in this standard.

The integrator to coordinate connection to local area network with Owner's network administrator to include IP Addressing, MAC address(s), switch port assignments, 802.1X and certificate configuration and multirole user authentication passwords.

The software interface to consist of one or more of the following types:

Client Based Configuration/Control software utilizing Windows 10 or higher.

Internal web server using browser client.

Software control of the sound masking system to include password-protected adjustment and configuration of the following minimum features:

Ability to import multiple floor plans to facilitate control of masking zones.

Choice of masking controller(s) in the system. The system may include multiple controller types.

Choice of emitters or speakers connected to each controller.

Pre-optimization of emitter or speaker equalization when applicable for direct field systems.

Muting/unmuting per zone.

Sound masking level control on a per-zone basis.

Background music and paging audio input level control.

Choice of audio distribution to controller(s) via 802.1X or Dante©.

Routing of up to eight audio sources via a network connection to one or more zones.

Equalization adjustment on a per-output basis.

Emergency mute and push to talk for paging.

Zone naming on a per-output basis.

Time of day scheduling on a per-zone basis.

Network / clock management.

Audio routing of external network audio sources.

Error notification / monitoring.

The hardware interface to be capable of basic level adjustment on a per-output basis using the front panel menu screen that allows, at minimum, operation of both sound masking and audio input levels.

A third-party API to be published by the sound masking product manufacturer using the RESTful API syntax to allow monitoring of the masking system by building wide / room control system providers.

PERIPHERALS

Fire Alarm Control Panel Input:

The system controller to accept a contact closure from a Fire Alarm Control Panel (FACP).

The contact closure to be configured in the system controller to mute all masking, background music, and paging audio in the masking system.

The controller to communicate with other masking system controllers on the network to also mute their audio when a contact closure is sensed.

The systems to automatically be restored to normal operation when the contact closure is removed.

Retain first paragraph below if a standalone paging microphone option is chosen.

Paging Microphone: To be used only with masking systems designed to support convenience paging.

A balanced, low-impedance paging microphone to be connected to an audio input in the masking controller. 48-volt phantom power to be provided by the controller to power the microphone if necessary.

A contact closure to be accepted by the masking controller to permit the audio from the paging microphone to pass to the page zone(s) as configured from the controller setup software.

The controller shall communicate with other masking system controllers on the network to allow the page audio to be routed to page zones on those masking controllers as configured from the masking system controller setup software.

Retain paragraph below if a networked paging microphone is chosen.

Paging Stations: To be used only with masking systems designed to support convenience paging.

The paging station to be network based utilizing standard 802.1X or Dante© protocols.

The paging station to be configured as a four-button or 10-button keypad version with either a nominal 13.3 inches (338 mm) gooseneck microphone or push-to-talk handheld microphone.

A multi-line LCD screen to have language support for at least nine languages and indicate the status of the paging station and provide feedback for:

Unlocking the paging station.

Selecting and executing a page code.

Recording messages.

Message playback progress.

Status of a live paging microphone.

A security PIN to be configurable at each page station to lock out unauthorized users.

The paging station to have a push-to-talk button with status indication and shall be latchable to support hands-free or long pages.

The paging station to include DSP to optimize audio playback for the page.

Paging audio to be blocked from the network until a page is being made for enhanced privacy.

The masking system to support up to 16 paging stations on the same network.

Each page station to have the ability to be assigned a priority paging level via software.

The paging station to support up to 32 page zones. Each page zone to be composed of one or more masking zones.

Each page station to have the capability to record, store, and play back up to 10 messages. Message length can be variable, with a pool of 50 minutes of record time available. Recordings to be made at the paging station or downloaded to the paging station through the network via a computer. Recordings may be locked to protect from accidental erasure.

A built-in event scheduler to allow automated playback of any recorded message.

The paging station to include default preannounce tones and also support customized preannounce tones.

The paging station to support either desktop or wall mounting.

The four-button paging station to support four user-configurable page codes.

The 10-button paging station to support 999 page codes.

The paging station to be configured via the masking system controller software.

The paging station to be NRTL listed to UL 62638-1, CSA C22.2 62368-1, CE marked and shall be RoHS compliant.

The paging station to be TAA compliant.

The paging station to include the manufacturer's five-year warranty.

CABLE ASSEMBLIES

All cable assemblies to consist of the proper number of conductors, wire gauge, and type, as approved by the system manufacturer based on the system design.

Cabling for 1.25 inches (32 mm) diameter emitters to be rated either Category 3, Category 5e, or Category 6. Cables to be terminated to TIA568A or TIA568B standards as a "straight-thru" cable.

Cabling for 3 inches (76 mm) diameter or larger speakers to be a jacketed UTP stranded 18 or 16 AWG cable.

Cabling for 70-volt speaker systems to be a jacketed UTP stranded 18 or 16 AWG cable.

Cabling for emitter system power supplies to be a jacketed UTP stranded 14 AWG cable.

Ethernet cabling to be UTP Category 5e, Category 6, or Category 7 rated. Cables to be terminated to TIA568A or TIA568B standards. Each Ethernet cable shall be verified to 10/100 MB/sec standards.

Line Level analog audio cabling to be a jacketed two-conductor 22 AWG stranded, twisted pair shielded cable designed for analog audio signals.

Cabling flammability rating to meet or exceed the installation conditions as required by NFPA/NEC/CSA or local codes/ jurisdiction as follows;

Type CM - General Purpose for Commercial Installation. Meets UL 1581 requirements for smoke and flammability testing.

Type CMR/FT4 - Commercial Installation for vertical risers. Meets UL 1666 requirements for smoke and flammability testing.

Type CMP/FT6 - Commercial Installation for plenum airspaces. Meets UL 910 requirements for smoke and flammability testing.

Terminations to be completed utilizing the appropriate connector type, method, and tooling as recommended by the product manufacturer.

All cabling to be plenum rated when located in a plenum space.

LABELS

Except where otherwise specified, label each item of control equipment as shown on Drawings.

Identify all wires and cables at every connection point to controllers with reference number keyed to the as-built wiring diagrams.

Room numbers appear on the contract documents for reference only. All labels shall reflect the Owner's final room designations.

Cable Markers:

High-grade PVC clip-on or permanent-type cable markers with permanent markings, or printed vinyl tape protected by clear shrink tubing or adhesive wrap to be used for labeling cabling.

SAFETY LISTINGS

Products and system to comply with all applicable local, regional, and national safety codes.

All electronics to be UL Listed or listed by an equivalent body such as Intertek ETL. Outside the USA, the electronics shall be certified by an equivalent certification body to meet local and/or national safety standards.

A ceiling device seismic support system to be installed in a manner certified by the manufacturer. Alternate seismic support system(s) must be approved by authorities having jurisdiction and based on local code requirements.

The masking control processor to have the capability to mute or otherwise disable the sound masking signal and any line-level audio input(s) of the entire sound masking system using a dry contact closure from a third-party source such as a fire alarm control panel to one of the masking controllers.

The sound masking system is not a primary means of emergency voice evacuation or ECS. For this reason, UL 2572 compliance is not required under this specification.

ENVIRONMENTAL CERTIFICATION

Sound masking system to be Green Spec Listed.

Sound masking system to be LEED compliant when Project requirements dictate.

EXECUTION

EXAMINATION

Prior to installation, verify the site is suitable for system installation.

Verify all locations where system components are to be installed are free of conflicts with other trades prior to installation.

Verify that colors chosen (where applicable) have been coordinated with the Architect, building manager, and/or building owner.

Verify that site building conditions match the system design plans including ceiling finishes, wall locations, and obstructions. Immediately notify the project manager of any discrepancies prior to the commencement of work.

Ensure system power requirements, network connectivity, and any other third-party infrastructure requirements for the system have been provided and installed prior to installation.

DELIVERY, STORAGE AND HANDLING

Protect all system components from moisture, dust, and damage during shipping, storage, and handling.

Deliver in manufacturer's original unopened and undamaged packages with manufacturer's labels legible and intact.

Inspect all system components upon receipt and upon unpacking.

INSTALLATION

General:

Comply with all applicable electrical and other safety codes.

Install the sound masking system in compliance with manufacturer's recommendations and published documentation.

Utilize competent workers to install all equipment at locations shown on the drawings in strict accordance with approved shop drawings. Record all necessary changes to the system design in cases where different from the submittal documents and submit changes for approval prior to implementing the changes.

Ensure that all equipment will be firmly held in place, including emitters or speakers, enclosures, amplifiers, processors, cables, etc. Fastenings and supports will be adequate to support their loads with a safety factor of at least five unless otherwise stated.

Ensure that all system components will be mounted in a level and plumb fashion utilizing the dimensions indicated on the associated drawings.

Mount user-controllable devices at a location and height that allows for normal adjustment and operation.

Locate all electronics to be conveniently accessible for service.

Ensure that all equipment located in the ceiling plenum will be UL 2043 rated for air handling environments.

Ceiling Mounted Masking Emitters or Loudspeaker:

Locate masking emitter or loudspeaker assemblies as indicated on Project Drawings and as required to meet the spatial uniformity requirements of this specification.

Ensure that design approval from the sound masking manufacturer is acquired for any direct field masking emitters or loudspeakers scheduled to be installed greater than 20 ft (6.1 m) above the finished floor prior to installation.

Ensure that design approval from the sound masking manufacturer is acquired for any indirect field masking loudspeakers scheduled to be installed greater than 30 ft (9.1 m) above the finished floor prior to installation.

Ensure that the emitter or speaker coverage pattern is not obstructed by building systems or structures that may impede performance of the sound masking system.

Ensure that minimum distance between the top of an emitter or loudspeaker and the structure or obstacles is maintained to allow adequate clearance of cabling and connectors.

Ensure that the masking emitters and loudspeakers are installed using manufacturer-supplied accessories when mounted in other substrates, ceiling types, and/or building structures. Sound masking emitter and speaker assemblies will be mounted to structure in an approved method as required by local codes and jurisdiction and indicated by the Project submittals.

Follow manufacturer recommendations for individual emitter or loudspeaker level controls/taps. Adjust as necessary.

Cabling:

Install all cabling in a professional, skillful manner with adequate service loops where applicable. Cabling will be dressed in a neat and consistent fashion using appropriate methods and materials.

Test all field-fabricated and manufacturer-supplied cables, before installation, for open circuits, shorts, crossed pairs, reversed pairs, split pairs, and proper pin-out.

Refer to manufacturer recommendations as to maximum cabling distances and types to support control processor unit(s), controls, and emitters or loudspeakers. Manufacturer's cable distance limitations and quantity of devices per cable run will never exceed manufacturer guidelines.

Coordinate cabling pathways to prevent conflict with other building systems. Care will be taken to minimize and eliminate all RFI and EMI interference sources.

Maintain appropriate separation between dissimilar signal types, voltages, and electrical devices.

Install and support cabling in a manner and frequency utilizing approved methods and materials as required by the local authority having jurisdiction.

Install cabling in metallic rigid or flex conduit only as indicated on the associated Project drawings/specification and using manufacturer-approved accessories.

Support all cabling from structure. Cabling will not contact ceiling tiles or inhibit their removal for access to the plenum.

SITE QUALITY CONTROL

Ensure that emitter and/or loudspeaker spacing is correct, consistent, and follows design guidelines set forth by the product manufacturer.

Securely terminate all cables.

SYSTEM STARTUP

Coordinate with building network administrator to provide an Ethernet connection to the building LAN where required.

Perform the entire product manufacturer's recommended testing and startup procedure as outlined in the manufacturer's product manual(s).

Ensure functional operation of all ancillary devices to include front panel controls, audio inputs, contact closures, wall controls, software control, and third-party controllers. Test each setting and confirm expected results from actions taken. Correct all deficiencies in operation.

Perform system startup at a time when each zone/space is completely vacant and free of any noise contamination.

SYSTEM TESTS AND ADJUSTMENTS

Qualifications of Testing Party:

Testing, calibration, and setup will be performed by a qualified manufacturer's employee or an authorized dealer or consultant who has been trained by the manufacturer.

Prior to Test and Adjustment: Ensure the site conditions are suitable for adjustment of the sound masking system. Adjustment can only be made when the following site conditions exist:

All ceiling assemblies are currently installed and completed.

All interior furnishings are assembled and in place.

Mechanical systems have been previously optimized to final operational conditions and are active in areas served by sound masking signals.

No occupants are present at the time of adjustment.

External noise sources (e.g. construction activities) are not present during testing.

Refer to "Qualifications" Article for more information.

Final testing will be scheduled at least 30 days in advance of owner occupancy.

Initial Test and Adjustments: Perform and record results of the following tests:

Masking Emitter/Loudspeaker Operation: Near field output of each masking emitter or loudspeaker will match the zone average within plus or minus 2.0 dB. Listen directly below each installed emitter or loudspeaker to confirm it is operating. For any emitter or loudspeakers found to be inoperative, or possibly operating at an incorrect level, use a calibrated sound level meter set to A-weighting and slow response to check the output. Place the microphone so to contact each grille and measure the variation between a minimum of two adjacent emitters or loudspeakers of the same zone.

Replace any defective emitters or loudspeakers or cabling, or otherwise correct cause for any emitters or loudspeakers found to be operating outside the range stated.

Buzzes, Rattles, and Distortion: With system operating at maximum level, listen for any buzzes, rattles, and objectionable distortion in all areas covered. Correct all causes of these defects.

Final Test and Adjustment: Perform and record the results of the following tests:

Control Settings: Adjust all masking spectrum levels and audio level controls for initial operation using manufacturer-recommended procedures. Document setting for each user control.

Adjustment of Sound Masking Levels: With the masking system active, measure the A-weighted sound pressure level of each zone independently. Use an ANSI S1.4 approved and calibrated Type 1 or Type 2 sound level meter and/or calibrated real-time acoustic analyzer with one-third octave filters per ANSI S1.11. Perform all SPL measurements at a typical seated height of 4 ft (1.2 m) above finish floor. Adjust the sound masking frequency spectrum in each zone to correspond with the A-weighted average level and frequency levels (non-weighted) shown in Table 1. Document, at minimum, one measurement per 1000 sq ft (93 sq m) in open offices, one measurement in 50 percent of private offices, and one measurement in 50 percent of all other spaces where sound masking is present. All documented measurements will meet the maximum level variation column criteria of Table 1. Correct any sound masking system deficiencies such as emitter or loudspeaker placement or loudspeaker tap settings to meet this performance criteria.

When integrating the sound masking system in a space previously occupied by workers, configure the incremental level adjustment feature of the control processor. Following the initial adjustment of sound masking levels, adjust each zone's initial sound masking level to a level 1.5 dBA above the average ambient noise level of the space. Engage the incremental level adjustment feature to automatically increase the sound masking level until reaching the "Average A-Weighted Sound Pressure Level" shown in Table 1 for each type of space listed. Use a minimum time frame of five days for the incremental level adjustment to reach the final target levels.

Provide a final testing report that states that the performance requirements of the sound masking system have been met.

Automatic Real-Time Masking Level Adjustment: Automatic adjustment of masking level based on ambient noise conditions will not be permitted under this specification. Only scheduled adjustment of sound masking levels may occur at times when each zone is vacant of occupants.

Proof of Performance Testing by a Qualified Acoustic Consultant: The Contractor will employ the services of a qualified acoustic consultant at no additional cost to the Owner, documenting to the Owner's Representative in written form that the system is fully operable and is installed in compliance with the terms of the performance specifications hereunder.

Test the system to demonstrate that the design goal of Privacy Index (PI) equal to 80 percent (Normal Privacy) or better is met between representative workstations separated by partitions of 5.5 ft (1.7 m) or greater height. For this test, select adjacent workstation pairs without direct line of sight or significant sound reflecting ceiling or wall elements between, and with a ceiling material rated at NRC of 0.85 or higher. Tests will be in accordance with ASTM E1130 except that the octave band calculation method of ANSI S3.5 may be used. Lower levels of PI are acceptable only if the ceiling or partition requirements described herein before are not met. Document the results of this test.

Test the system in each open plan area zone served to demonstrate that the design goal for spatial uniformity is met. Tests will be carried out per ASTM E1573 as measured in the 2,000 Hz octave band. At each location, the average sound pressure levels will be measured over an interval of at least four seconds at four positions at 90-degree intervals around a circle of 1 ft (0.3 m) radius centered on the location. The arithmetic mean sound pressure level will be calculated from the four measured values. For at least 75 percent of the test locations, the arithmetic mean sound pressure level in the 2,000 Hz octave band will not vary by more than +/-1 dB from the average of the arithmetic mean sound pressure levels measured at all locations. Document the results of this test.

Test the system to demonstrate that the Speech Privacy Class (SPC) is at least 75 (Standard Speech Privacy) between representative private (enclosed) offices served by the system. For this test, select adjacent offices with closed doors free of air gaps. Tests will be in accordance with ASTM E2638-10. Test 10 percent of all similar sized offices and meeting spaces utilizing the same basic construction methods. Lower levels of SPC are acceptable if the common walls between the offices are composed of assemblies <=STC 40 and which do not extend to the deck above or in cases where the common wall <=STC 40, does not extend to the deck, and the ceiling attenuation class of the ceiling material is less than 45 (<=CAC 45). If the SPC achieved is lower than 75 due to architectural factors, bring this to the attention of the Owner or General Contractor. Document the results of this test.

The sound masking contractor will make all necessary modifications to the system design, integration, and/or settings, as specified by the System Designer, to achieve the performance testing goals contained herein at no additional expense to the Owner. Designer, to achieve the performance testing goals contained herein at no additional expense to the Owner.

CLEANING AND WASTE MANAGEMENT

Remove empty packaging and other material waste.

Clean all debris created by installation of components.

Clean system components where required.

FINAL CLOSEOUT AND AS BUILT DOCUMENTATION

Document, prepare, and submit all final control processor settings, emitter or loudspeaker zone maps, loudspeaker tap settings, one line diagrams, operational instruction, and testing results in PDF format. Submit three copies to the system designer, the project manager and, if required, the Owner's representative for final review and acceptance.

Indicate the location of each sound pressure level measurement, privacy index measurement, and spatial uniformity measurement referenced within the final documents on the zone map.

In cases where the sound masking system utilizes configuration software for adjustment and operation, provide a copy on media with each documentation set utilizing the same software version as currently installed and operating. The Contractor provides all configuration files created by the configuration software on the same media.

With 30-day advance notice, train Owner's designated representative on sound masking system maintenance and proper operation.

Provide user instruction on operation.

Discuss potential for misadjustment of sound masking levels and deterioration of both comfort and speech privacy performance.

Demonstrate all software features, controls, and configuration.

ATTACHMENTS

System Design Schematic: Schematic of the system design on a floor plan showing the quantity and location of system components indicating zoning requirements.

Project Drawing Sheet(s): <Insert drawing sheets here>.

CHART ONE for all system types

| Frequency | Open Office | Private Office | Corridor / Conference Room | Max Level Variation - Direct Field & Target Level Variation - Indirect Field | Max Level Variation - Indirect Field |
| --- | --- | --- | --- | --- | --- |
| *125 Hz | 48 dB | 43 dB | 46 dB | +/- 3 dB | +/- 5 dB |
| *160 Hz | 47 dB | 42 dB | 45 dB | +/- 3 dB | +/- 4 dB |
| 200 Hz | 45 dB | 40 dB | 43 dB | +/- 3 dB | +/- 3 dB |
| 250 Hz | 44 dB | 39 dB | 42 dB | +/- 2 dB | +/- 3 dB |
| 315 Hz | 42 dB | 37 dB | 40 dB | +/- 1 dB | +/- 3 dB |
| 400 Hz | 41 dB | 36 dB | 39 dB | +/- 1 dB | +/- 3 dB |
| 500 Hz | 40 dB | 35 dB | 38 dB | +/- 1 dB | +/- 2.5 dB |
| 630 Hz | 39 dB | 34 dB | 37 dB | +/- 1 dB | +/- 2.5 dB |
| 800 Hz | 38 dB | 33 dB | 36 dB | +/- 1 dB | +/- 2.5 dB |
| 1000 Hz | 37 dB | 32 dB | 35 dB | +/- 1 dB | +/- 2.5 dB |
| 1250 Hz | 36 dB | 31 dB | 34 dB | +/- 1 dB | +/- 2.5 dB |
| 1600 Hz | 34 dB | 29 dB | 32 dB | +/- 1 dB | +/- 2.5 dB |
| **2000 Hz | 32 dB | 27 dB | 30 dB | +/- 1 dB | +/- 2 dB |
| **2500 Hz | 30 dB | 25 dB | 28 dB | +/- 1 dB | +/- 2 dB |
| **3150 Hz | 27 dB | 22 dB | 25 dB | +/- 1 dB | +/- 2 dB |
| **4000 Hz | 24 dB | 19 dB | 21 dB | +/- 1 dB | +/- 2 dB |
| **5000 Hz | 19 dB | 14 dB | 17 dB | +/- 1 dB | +/- 2 dB |
| *6300 Hz | 14 dB | 9 dB | 12 dB | +/- 1 dB | Not Applicable |
| *8000 Hz | 11 dB | 6 dB | 9 dB | +/- 1 dB | Not Applicable |
| Average "A" Weighted Sound Pressure Level (dB A) | 47 dBA | 42 dBA | 45 dBA | +/- 2 dBA | +/- 3 dBA |

* Denotes additional frequency bands to be used when commissioning systems designed for background music and paging applications.

** For effective speech privacy, special attention must be given to these frequency bands to ensure evenness of coverage. If the variation is greater than what is specified above, it is likely that the emitters or loudspeakers are spaced too far apart to meet the above requirements.

END OF SECTION 275119